## Sheet1
D |  | Powe Equipment (AC ) | UoM | Qty/Site | Qty | Total Qty
1 | FA00260 | SMF VRLA- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 Banks (48 nos) = 900 AH per site with battery racks, stands, 2 nos of brackets (angle iron) to fix/support the battery stand on the wall, battery connectors, battery remover, transparent covers, etc. Make:HBL/Amaraja/Rocket/NED/ or of Equivalent brand | Banks | 1 | 46 | 46
2 | FA00825 | SMF VRLA Battery- 2V/760 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 760 AH * 2 nos = 1520 AH per site with battery racks, stands, 2 nos of brackets (angle iron) to fix/support the battery stand on the wall, battery connectors, battery remover, transparent covers, etc. Make:HBL/Amaraja/Rocket/NED/or of Equivalent brand | Banks | 1 | 1 | 1
3 | FA00602 | SMPS Rectifier Battery Charger, IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type with minimum 8 No of Modules and 8 slots of 60 Amps per module. Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. ( Vertiv/Delta / benning/Dynamic Power/Exicom/ or of Equivalent brand) | Set | 1 | 49 | 49
4 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | nos | 1 | 49 | 49
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | nos | 1 | 49 | 49
6 | FA00441 | DC Power Cable 70 Sq.mm ( RED) 1.1KV, IC PVC Insulated, unarmoured multi-strand copper Cable ( 40M per site) (Make: Polycab/ RR/Havell's/KEI/or of Equivalent brand | nos | 1 | 49 | 49
7 | FA00442 | DC Power Cable 70 Sqmm ( Blue/Black) 1.1KV, IC PVC Insulated, unarmoured multi-strand copper Cable ( 40M per site) (Make: Polycab/ RR/Havell's/KEI/or of Equivalent brand | nos | 1 | 49 | 49
8 | FA00279 | Rectifier Cable (RED) , 20 Sqmm, 25 Meters per site (Make: Polycab/ RR/Havell's/KEI | nos | 1 | 49 | 49
9 | FA00280 | Rectifier Cable (Blue/Black), 20 Sq.mm, 25 Meters per site (Make: Polycab/ RR/Havell's/KEI or of Equivalent brand | nos | 1 | 49 | 49
10 | FA00603 | AC Power Cables for Aircon ( 1.1 kV, 3 C PVC Insulated, unarmored multi-strand copper cable), 4 sq.mm, 25m per site (Make: Polycab/ RR/Havell's/KEI or of Equivalent brand | nos | 1 | 49 | 49
11 | FA00604 | Electrical Earthing Cable , 4 Sq.mm (Green Colour) 100 Mtrs per site (Make: Polycab/ RR/Havell's or of Equivalent brand) | nos | 1 | 49 | 49
12 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati/or of Equivalent brand | Set | 1 | 49 | 49
13 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv/or of Equivalent brand) | Set | 1 | 49 | 49
14 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin or of Equivalent brand) | Set | 1 | 49 | 49
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havell's/KEIor of Equivalent brand) | nos | 1 | 49 | 49
16 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral/Datakom or of Equivalent brand) | Set | 1 | 49 | 49
17 | FA00288 | TVSS/SPD: Surge Protection Device, Single Phase (230V AC), Max discharge current 100kA (10/350 µs), Fault Indicator Available, Protection Mode: L-N/N-PE, with appropriate MCB and Box, prewired (Make: LPI/Emerson/Erico/Eaton/Phoenix/Schneider or of Equivalent brand) | Set | 1 | 49 | 49
18 | FA00607 | Copper Terminal Ends (Ring Type)/Lugs, 4 sq.mm (20 nos Ring Type ) | Pkt | 1 | 49 | 49
19 | FA00608 | Copper Terminal Ends (Ring Type)/Lugs, 4 sq.mm ( 10 nos pin type) | Pkt | 1 | 49 | 49
20 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 49 | 49
21 | FA00610 | Copper Terminal Ends (Ring Type)/Lugs, 25 sq.mm ( 5 nos pin type) | Pkt | 1 | 49 | 49
22 | FA00611 | Copper Terminal Ends Lugs, 70 sq.mm ( 15 nos Ring type) | Pkt | 1 | 49 | 49
23 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 49 | 98
24 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 49 | 98
25 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 49 | 98
26 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 49 | 49
27 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 49 | 49
28 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 49 | 49
29 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 49 | 49
30 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 49 | 49
E |  | Solar Power Equipment ( Solar 10KW)
1 | FA00260 | VRLA Battery- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 nos = 900 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc. Make:HBL/Amaraja/Rocket/NED or of Equivalent brand | Banks | 1 | 11 | 11
2 | FA00613 | Solar Modules/Panels with structures ie 1.5M above the ground level, Wattage (Wp): 335-350 Wp Voltage (Vmp) : 36 - 40 V Current (Imp) : 8 - 10 Amps with mounting structures (6 module structure), pre-assembled connectors ( 10KW capacity) ( Tata BP/ Vikram solar/ Mosebaer/Waree/or of Equivalent brand) 30 Module per site (Tata BP/ Vikram solar/ Mosebaer/Waree/or of Equivalent brand) | PV/module | 30 | 11 | 330
3 | FA00827 | Solar Structure ie 1.5M above ground level foundation bolts and templates for 6 module structure with 30 panels. | Set | 1 | 11 | 11
4 | FA00642 | Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available, Make Erico/Eritech/Tercel/Dehn/LPI/Phoenix/or of Equivalent brand | nos | 1 | 11 | 11
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | nos | 1 | 11 | 11
6 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | nos | 1 | 11 | 11
7 | FA00643 | Solar-DG-Utility-Battery Hybrid MPPT system, modular type, 2 kW, 500 Amps, having min 5 (Five) solar mppt modules of 40 Amps capacity and 3 additional MPPT slots . 6 nos of rectifier module of capacity 80 amps and 2 additional rectifier slots having the following features: Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Further, the system also should have min two nos of appropriate rating of HRC fuses for connecting of min two battery banks of min 450 Ah per bank. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP: 1. Solar Converter Specs: Input voltage (DC), Vertiv/Delta/Eltek/Dynamic Power/Exicom/or of Equivalent brand | Set | 1 | 11 | 11
8 | FA00614 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., Solar Panel to AJB: 6 sq.mm, (RED) 50 m per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 11 | 11
9 | FA00615 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., ) Solar Panel to AJB: 6 sq.mm, (BLACK) 50 m per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 11 | 11
10 | FA00617 | Solar Cable Armoured Specification for 10KW Solar system: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C. 4. Armour: braid of galvanized steel, , AJB to Hybrid Rectifier: 16sq.mm, 2C, solar dc cable, multistand copper conductor 100M (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 11 | 11
11 | FA00620 | DC Power Cable, Hybrid Charger to Battery Bank: 70 sq.mm, 1C, PVC insulated, multistrand copper conductor (RED ) 50 m per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 11 | 11
12 | FA00621 | DC Power Cable, Hybrid Charger to Battery Bank: 70 sq.mm, 1C, PVC insulated, multistrand copper conductor (BLACK ) 50 m per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 11 | 11
13 | FA00017 | Installation Materials | lot | 1 | 11 | 11
14 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati/or of Equivalent brand) | Set | 1 | 11 | 11
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havells/or of Equivalent brand) | nos | 1 | 11 | 11
16 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv/or of Equivalent brand) | Set | 1 | 11 | 11
17 | FA00622 | DC/AC lighting system in Shelter, 48V dc light or 230v AC tubelight with switch | Set | 1 | 11 | 11
18 | FA00649 | AC lighting system in Shelter, 230v AC tubelight with switch & accessories | Set | 1 | 11 | 11
19 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral/Datakom/or of Equivalent brand) | Set | 1 | 11 | 11
20 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin/or of Equivalent brand) | Set | 1 | 11 | 11
21 | FA00645 | Solar Junction Box , Array Junction Box (min 4 inputs and 1 output), | Set | 5 | 11 | 55
22 | FA00625 | Copper Terminal Lugs, 6 sq.mm ( 20 nos Ring type) | Pkt | 1 | 11 | 11
23 | FA00626 | Copper Terminal Lugs, 6 sq.mm ( 10 nos pin type) | Pkt | 1 | 11 | 11
24 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 11 | 11
25 | FA00840 | Copper Terminal Lugs, 25 sq.mm ( 10 nos pin type) | Pkt | 1 | 11 | 11
26 | FA00611 | Copper Terminal Ends Lugs, 70 sq.mm ( 15 nos Ring type) | Pkt | 1 | 11 | 11
27 | FA00651 | Copper Terminal Lugs, 16 sq.mm (25 nos pin Type ) | Pkt | 1 | 11 | 11
28 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 11 | 22
29 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 11 | 22
30 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 11 | 22
31 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
32 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
33 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
34 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 11 | 11
35 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
F |  | Solar Power (12KW)
1 | FA00825 | VRLA Battery- 2V/760 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 760 AH * 2 nos = 1520 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc Make:HBL/Amaraja/Rocket/NED/or of Equivalent brand | Banks | 1 | 3 | 3
2 | FA00613 | Solar Modules/Panels with structures ie 1.5M above the ground level, Wattage (Wp): 335-350 Wp Voltage (Vmp) : 36 - 40 V Current (Imp) : 8 - 10 Amps with mounting structures (6 module structure), pre-assembled connectors ( 10KW capacity) ( Tata BP/ Vikram solar/ Mosebaer/Waree/Equivalent) 36 Module per site (Tata BP/ Vikram solar/ Mosebaer/Waree/or of Equivalent brand) | PV/module | 36 | 3 | 108
3 | FA00839 | Solar Structure ie 1.5M above ground level foundation bolts and templates for 6 module structure with 36 panels. | Set | 1 | 3 | 3
4 | FA00642 | Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available, Make Erico/Eritech/Tercel/Dehn/LPI/Phoenix/or of Equivalent brand | No | 1 | 3 | 3
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | No | 1 | 3 | 3
6 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | No | 1 | 3 | 3
7 | FA00829 | Solar-DG-Utility-Battery Hybrid MPPT system, modular type, 2 kW, 500 Amps, having min 6 (Five) solar mppt modules of 40 Amps capacity and 2 additional MPPT slots . 6 nos of rectifier module of capacity 80 amps and 2 additional rectifier slots having the following features: Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Further, the system also should have min two nos of appropriate rating of HRC fuses for connecting of min two battery banks of min 450 Ah per bank. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP: 1. Solar Converter Specs: Input voltage (DC), Vertiv/Delta/Eltek/Dynamic Power/Exicom/or of Equivalent brand | set | 1 | 3 | 3
8 | FA00830 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., Solar Panel to AJB: 6 sq.mm, (RED) 50 m per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | nos | 1 | 3 | 3
9 | FA00831 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., ) Solar Panel to AJB: 6 sq.mm, (BLACK) 50 m per site (Polycab/ RR/Havell's /Relison/or of Equivalent brand) | nos | 1 | 3 | 3
10 | FA00832 | Solar Cable Armoured Specification for 12KW Solar system: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C. 4. Armour: braid of galvanized steel, , AJB to Hybrid Rectifier: 16sq.mm, 2C, solar dc cable, multistand copper conductor 120M per site (Polycab/ RR/Havell's/Relison/or of Equivalent brand) | No | 1 | 3 | 3
11 | FA00843 | DC Power Cable, Hybrid Charger to Battery Bank: 90 sq.mm, 1C, PVC insulated, multistrand copper conductor (RED ) 50 m per site (Polycab/ RR/Havell's /Relison/or of Equivalent brand) | No | 1 | 3 | 3
12 | FA00834 | DC Power Cable, Hybrid Charger to Battery Bank: 90 sq.mm, 1C, PVC insulated, multistrand copper conductor (BLACK ) 50 m per site (Polycab/ RR/Havell's /Relison/or of Equivalent brand) | No | 1 | 3 | 3
13 | FA00017 | Installation Materials | No | 1 | 3 | 3
14 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati/or of Equivalent brand) | No | 1 | 3 | 3
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havells/or of Equivalent brand) | No | 1 | 3 | 3
16 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv/or of Equivalent brand) | Set | 1 | 3 | 3
17 | FA00622 | DC/AC lighting system in Shelter, 48V dc light or 230v AC tubelight with switch | Set | 1 | 3 | 3
18 | FA00649 | AC lighting system in Shelter, 230v AC tubelight with switch & accessories | Set | 1 | 3 | 3
19 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral/or of Equivalent brand) | No | 1 | 3 | 3
20 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin/or of Equivalent brand) | Set | 1 | 3 | 3
21 | FA00645 | Solar Junction Box , Array Junction Box (min 4 inputs and 1 output), | Set | 6 | 3 | 18
22 | FA00625 | Copper Terminal Lugs, 6 sq.mm ( 20 nos Ring type) | Pkt | 1 | 3 | 3
23 | FA00626 | Copper Terminal Lugs, 6 sq.mm ( 10 nos pin type) | Pkt | 1 | 3 | 3
24 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 3 | 3
25 | FA00840 | Copper Terminal Lugs, 25 sq.mm ( 10 nos pin type) | Pkt | 1 | 3 | 3
26 | FA00611 | Copper Terminal Ends Lugs, 90 sq.mm ( 15 nos Ring type) | Pkt | 1 | 3 | 3
27 | FA00651 | Copper Terminal Lugs, 16 sq.mm (25 nos pin Type ) | Pkt | 1 | 3 | 3
28 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 3 | 6
29 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 3 | 6
30 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 3 | 6
31 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
32 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
33 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
34 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 3 | 3
35 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
F |  | DG set
1 | FA00835 | DG 20 KVA , Single Phase (230V, 50Hz), 1500rpm and 0.8 PF, sound and weather proof canopy outdoor unit including cold starting kit, AMF Panel with inbuilt DC-DC Converter (48V input & 12V output), Fuel Tank (300Litres), 25Sqmm single phase armoured PVC insulated copper cable with 15 meters per site, Earth Cables 15 mtrs each site with other accessories including lugs ( Jackson (Cummins)/ TMTL Eicher) | Set | 1 | 22 | 22
2 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper coated (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati/or of Equivalent brand) | Set | 1 | 22 | 22