## BOQ
Sl. No | Item Code | Description | UoM | Sites
A |  | Tower
1 | FA01049 | 40M 4 Legged Tower foundation (anchor bolts, templates, etc) | Set | 1
2 | FA00816 | 35M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 5
3 | FA00817 | 30M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 16
4 | FA00818 | 25M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 24
5 | FA00819 | 20M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 3
6 | FA01048 | 40M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 4-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the RFP. | Set | 1
7 | FA00601 | 35M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the RFP. | Set | 5
8 | FA00296 | 30M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the RFP. | Set | 16
9 | FA00297 | 25M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the RFP. | Set | 24
10 | FA00298 | 20M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the RFP. | Set | 3
B |  | Shelter
1 | FA00822 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:3600x2600x2500(LxWxH in mm) foundation materials. | Set | 5
2 | FA00300 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:3600x2600x2500(LxWxH in mm). Panel with Foam-60mm, Material of skin- 0.6mmx0.6mm pre- Floor- Ply 18mm and PVC 2mm (as per drawing attached in RFP) | Set | 5
3 | FA00823 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:6000x3600x2600(LxWxH in mm) foundation materials | Set | 1
4 | FA00824 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:6000x3600x2600(LxWxH in mm). Panel with Foam-60mm, Material of skin- 0.6mmx0.6mm pre- Floor- Ply 18mm and PVC 2mm (as per drawing attached in RFP) | Set | 1
C |  | Monopole
1 | FA00821 | 15M Monopole foundation (anchor bolts, templates, etc) | Set | 47
2 | FA00303 | 15M With separate Earthing provisions (as per design attached in RFP) Tower should have name plate [company name (Bhutan Telecom Limited, Height and year of installation), 3 LED Lamp with LDR Sensor and lighting cables and accessories] | Set | 29
3 | FA00304 | 15M With separate Earthing provisions (as per design attached in RFP) Tower should have name plate [company name (Bhutan Telecom Limited, Height and year of installation), 2 LED Lamp with LDR Sensor and lighting cables and accessories] | Set | 13
4 | FA01050 | 15M With separate Earthing provisions (as per design attached in RFP) Tower should have name plate [company name (Bhutan Telecom Limited, Height and year of installation), without LED Lamp with LDR Sensor and lighting cables and accessories] | Set | 2
5 | FA00826 | 15M Flange Joint With separate Earthing provisions (as per design attached in RFP) Tower should have name plate [company name (Bhutan Telecom Limited, Height and year of installation), 3 LED Lamp with LDR Sensor and lighting cables and accessories] | Set | 3
D |  | AC Power Equipment
1 | FA01072 | VRLA- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 Banks = 900 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc (Make: HBL/ Amaraja/Rocket) | Bank (24cells/ bank) | 3
2 | FA01073 | Rectifiers (500 amps, 24 kW) floor mounted with stand (1 mtr height above floor) IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type including 8/6 no of modules having 60/80 Amps per module. Must have load facility to connect both critical and non-critical loads below mentioned ratings of DC MCBs and HRC Fuse. i. SP MCBs: 63 amps – 2 Nos, 32 amps – 4 Nos, 20 amps – 5 Nos, 16 amps – 5 Nos ii. HRC Fuse: 100 amps – 2 Nos Also, should have an inbuilt controller and safety devices such as BLVD and LLVD having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. Should include class C AC SPD and DC SPD and must be compatible with Li Batteries without having to upgrade the software. (Make: Vertiv/Delta/Exicom/Huawei/Equivalent) | Set | 3
3 | FA00275 | DCPDB (Rating: 100 amps, -48VDC. This Pre-Wired Power Distribution Board shall provide all the load conections with proper rating of MCBs and additional battery charging facilities. DC MCB DP (63A-2 nos,32 A-6nos.16A-10nos)) (Make: Any Quality Brand as per given drawing specification MCB brand) | Nos | 3
4 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | Nos | 3
5 | FA01074 | DC Power Cable 70 Sq.mm ( RED) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (40 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
6 | FA01075 | DC Power Cable 70 Sq.mm (BLACK) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (40 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
7 | FA01076 | DC Power Cable 25 Sq.mm ( RED) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (25 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
8 | FA01077 | DC Power Cable 25 Sq.mm (BLACK) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (25 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
9 | FA01078 | DC Power Cable 4 Sq.mm (BLACK) 1.1KV, 3C PVC Insulated, unarmoured multi-strand copper Cable (25 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
10 | FA01079 | DC Power Cable 4 Sq.mm (Green) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (100 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 3
11 | FA01080 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (Make: ICON/PRAGATI/ERICO/LPI) | Set | 3
12 | FA00605 | Free cooling unit: Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling. (Make: Pragati/ICON/Delta/Vertiv or of equivalent) | Set | 3
13 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin or of Equivalent brand) | Set | 3
14 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) | Nos | 3
15 | FA00901 | LPS (Lightning protection system): 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 50 mtrs giving level I protection. Tested ininternational high tension laboratory, tested/approved by CPRI, India 2. FRP Mast- 2 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down copper conductor (50 sq.mm copper) 5. Chemical Earthing: 1. Tri-rod 99.9% copper (5 ft long 12 mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting 2. GEM (Chemical) # 2X40 kg 3. Copper revit # 10 nos 4. Earth Distribution bus bar # 2 Nos, 5. Earth pit cover - 2 nos. 5. Copper 99.9% copper) strip 25X3 mm- 30 mtr 6.Salt- 2 X 10 kg per set, 7. Charcoal # 2 x 5 kg per set. 8. Connectors, lugs,clamps, etc (Make: LPI/Erico/Bakiral or of equivalent) | Set | 3
16 | FA00288 | TVSS/SPD: Surge Protection Device, Single Phase (230V AC), Max discharge current 100kA (10/350 µs), Fault Indicator Available, Protection Mode: L-N/N-PE, with appropriate MCB and Box, prewired (Make: LPI/Emerson/Erico/Eaton/Phoenix) | Set | 3
17 | FA01064 | Copper Terminal Ends (Ring Type)/Lugs: 4 sq.mm (20 nos Ring Type ) | Lot | 3
18 | FA01065 | Copper Terminal Ends (Pin Type)/Lugs: 4 sq.mm (10 nos Ring Type ) | Lot | 3
19 | FA01066 | Copper Terminal Ends (Ring Type)/Lugs: 25 sq.mm ( 15 nos Ring Type ) | Lot | 3
20 | FA01067 | Copper Terminal Ends (Pin Type)/Lugs: 25 sq.mm ( 5 nos Pin Type ) | Lot | 3
21 | FA01068 | Copper Terminal Ends (Ring Type)/Lugs: 70 sq.mm (15 nos Ring) | Lot | 3
22 | FA01069 | PVC Insulation Tape: Red (2 rolls per site) | Lot | 3
23 | FA01070 | PVC Insulation Tape: Black (2 rolls per site) | Lot | 3
24 | FA01071 | PVC Insulation Tape: Green (2 rolls per site) | Lot | 3
25 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 3
26 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 3
27 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 3
28 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 3
29 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 3
D |  | Additional Power Equipment
1 | FA01072 | VRLA- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 Banks = 900 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc (Make: HBL/ Amaraja/Rocket) | Bank (24cells/ bank) | 1
2 | FA00275 | DCPDB (Rating: 100 amps, -48VDC. This Pre-Wired Power Distribution Board shall provide all the load conections with proper rating of MCBs and additional battery charging facilities. DC MCB DP (63A-2 nos,32 A-6nos.16A-10nos)) (Make: Any Quality Brand as per given drawing specification MCB brand) | Nos | 37
3 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | Nos | 28
4 | FA01074 | DC Power Cable 70 Sq.mm ( RED) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (40 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 7
5 | FA01075 | DC Power Cable 70 Sq.mm (BLACK) 1.1KV, 1C PVC Insulated, unarmoured multi-strand copper Cable (40 mtr/site) (Make: Polycab/ RR/Havell's or of Equivalent brand) | Nos | 7
6 | FA01073 | Rectifiers (500 amps, 24 kW) floor mounted with stand (1 mtr height above floor) IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type including 8/6 no of modules having 60/80 Amps per module. Must have load facility to connect both critical and non-critical loads below mentioned ratings of DC MCBs and HRC Fuse. i. SP MCBs: 63 amps – 2 Nos, 32 amps – 4 Nos, 20 amps – 5 Nos, 16 amps – 5 Nos ii. HRC Fuse: 100 amps – 2 Nos Also, should have an inbuilt controller and safety devices such as BLVD and LLVD having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. Should include class C AC SPD and DC SPD and must be compatible with Li Batteries without having to upgrade the software. (Make: Vertiv/Delta/Exicom/Huawei/Equivalent) | Set | 4
7 | FA01081 | Rectifiers (300 amps, 14.4 kW) 19” rack mount with accessories IP Vac = 180 – 280 Vac; OP = (-48V DC), 300 Amps, Modular Type including 5/4 no of modules having 60/80 Amps per module. Must have load facility to connect loads as below mentioned ratings of DC MCBs i. SP MCBs: 32 amps – 4 Nos, 20 amps – 5 Nos, 16 amps – 4 Nos Battery MCB Rating: 120 amps dc – 2 Nos Also, should have an inbuilt controller and safety devices such as BLVD having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. Should include class C AC SPD and DC SPD and must be compatible with Li Batteries without having to upgrade the software. (Make: Vertiv/Delta/Exicom/Huawei/Equivalent) | Set | 6
8 | FA01082 | Hybrid Rectifiers (500 amps, 24 kW) floor mounted with stand (1 mtr height above floor) IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type including 4/3 no of modules having 60/80 Amps per module. Solar: MPPT Modules: (4/3 no of modules having 60/80 amps per MPPT), Input - 60 to 400 Vdc, Output - 42 to 58V dc. Must have load facility to connect both critical and non-critical loads below mentioned ratings of DC MCBs and HRC Fuse. i. SP MCBs: 63 amps – 2 Nos, 32 amps – 4 Nos, 20 amps – 5 Nos, 16 amps – 5 Nos, ii. HRC Fuse: 100 amps – 2 Nos. Also, should have an inbuilt controller and safety devices such as BLVD and LLVD having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. Should include class C AC SPD and DC SPD and must be compatible with Li Batteries without having to upgrade the software. (Make: Vertiv/Delta/Exicom/Huawei/Equivalent) | Set | 5
9 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin or of Equivalent brand) | Set | 1
10 | FA01080 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (Make: ICON/PRAGATI/ERICO/LPI) | Set | 11
11 | FA00901 | LPS (Lightning protection system): 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 50 mtrs giving level I protection. Tested ininternational high tension laboratory, tested/approved by CPRI, India 2. FRP Mast- 2 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down copper conductor (50 sq.mm copper) 5. Chemical Earthing: 1. Tri-rod 99.9% copper (5 ft long 12 mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting 2. GEM (Chemical) # 2X40 kg 3. Copper revit # 10 nos 4. Earth Distribution bus bar # 2 Nos, 5. Earth pit cover - 2 nos. 5. Copper 99.9% copper) strip 25X3 mm- 30 mtr 6.Salt- 2 X 10 kg per set, 7. Charcoal # 2 x 5 kg per set. 8. Connectors, lugs,clamps, etc (Make: LPI/Erico/Bakiral or of equivalent) | Set | 11
12 | FA01083 | LV Aerial Bundled Conductor with messenger wire: 1.1kV,2C PVC insulated, unarmored multi-strand aluminum cable 50 sqmm | Mtrs | 12120
E |  | Other Materials
1 | FA00400 | Roxtec (GH 6x1/18 AISI316) | Nos | 6
2 | FA00301 | Antenna Mounting Structure (Tower leg/angular tower) | Set | 90
F |  | Services
1 | SW00588 | Transporation of Tower and foundation materials to designated site | Nos | 49
2 | SW00639 | 40M 3Legged Tower Erection including earthing | Nos | 1
3 | SW00590 | 35M 3Legged Tower Erection including earthing | Nos | 5
4 | SW00591 | 30M 3Legged Tower Erection including earthing | Nos | 16
5 | SW00592 | 25M 3Legged Tower Erection including earthing | Nos | 24
6 | SW00593 | 20M 3Legged Tower Erection including earthing | Nos | 3
7 | SW00595 | Transporation of shelter and foundation materials to designated site | Nos | 6
8 | SW00596 | Shelter Erection including earthing | Nos | 5
9 | SW00597 | Shelter Erection :6000x3600x2600 including earthing | Nos | 1
10 | SW00598 | Transporation of AC Power to designated site | Nos | 3
11 | SW00600 | Installation of AC Power including earthing, etc as per details provided | Nos | 3
12 | SW00605 | Transporation of Monopole and foundation materials to designated site | Nos | 47
13 | SW00606 | Monopole Erection including earthing and lighting | Nos | 47

## Service BOM
Loading Details
Sl.No | Region | PC | Site Name | Infra Type | Tower Type (3 legged/4 legged) | Tower Height | Headload (from nearest roadpoint) | Distance from main road KM(Approx) | Tower Weight (Kg) | Transporation of Tower and foundation materials to designated site Price | Tower Erection including earthing Price
1 | CR | Dagapela | Tsangleykha | NI | 3 legged | 25m | 10mins | 8KM | 4450 | Yes | Yes
2 | CR | Damphu | Pherpheri | NI | 3 legged | 30m | 40mins | 40KM | 5750 | Yes | Yes
3 | CR | Damphu | Changchey | NI | 3 legged | 25m | 45mins | 15KM | 4450 | Yes | Yes
4 | CR | Bumthang | Pedtshaling Goenpa | NI | 3 legged | 20m | 15mins | 14KM | 3550 | Yes | Yes
5 | CR | Trongsa | Mangdiphu | NI | 3 legged | 25m | 40mins | 6.5km | 4450 | Yes | Yes
6 | CR | Sarpang | Jugaydara | NI | 3 legged | 25m | 20mins | 17km | 4450 | Yes | Yes
7 | CR | Sarpang | Kyipaithang | NI | 3 legged | 30m | NO | 1km | 5750 | Yes | Yes
8 | CR | Sarpang | Bunakha | NI | 3 legged | 25m | More than 1 Hour | 8km | 4450 | Yes | Yes
9 | CR | Gelephu | Barshong | NI | 3 legged | 25m | NO | 17KM | 4450 | Yes | Yes
10 | CR | Gelephu | Shetikhari | NI | 3 legged | 35m | NO | 3KM | 7750 | Yes | Yes
11 | CR | Gelephu | Norbuling | NI | 3 legged | 35m | NO | 21KM | 7750 | Yes | Yes
12 | CR | Zhemgang | Wangphu | NI | 3 legged | 25m | 30mins | 45km | 4450 | Yes | Yes
13 | CR | Zhemgang | Mewanggang | NI | 3 legged | 25m | 30mins | 35km | 4450 | Yes | Yes
14 | CR | Gelephu | Chuzaygang | NI | 3 legged | 35m | NO | 27KM | 7750 | Yes | Yes
15 | ER | Lhuntse | Minjaytse | NI | 3 legged | 25m | 50mins | 27km | 4450 | Yes | Yes
16 | ER | Mongar | Gangmung | NI | 3 legged | 25m | 20 mins | 60km | 4450 | Yes | Yes
17 | ER | Pemagatshel | Wongborang (Dungmin) | NI | 3 legged | 25m | 1 hur | 65km | 4450 | Yes | Yes
18 | ER | Sjongkhar | Jangchubling (Orong) | NI | 3 legged | 30m | yet confirm | YET TO CONFIRM | 5750 | Yes | Yes
19 | ER | Sjongkhar | Dungkharling | NI | 3 legged | 30m | More than 1 Hour | 4km | 5750 | Yes | Yes
20 | ER | Trashigang | Berdungma | NI | 3 legged | 25m | 30mins | 115Km from Trashigang | 4450 | Yes | Yes
21 | ER | Trashigang | Thrakthri | NI | 3 legged | 30m | 15 minutes | 52Km from Trashigang | 5750 | Yes | Yes
22 | ER | Trashigang | Durung | NI | 3 legged | 30m | 10 minutes | 36Km from Trashigang | 5750 | Yes | Yes
23 | ER | Trashigang | Yabrang | NI | 3 legged | 25m | 10 minutes | 38Km from Trashigang | 4450 | Yes | Yes
24 | ER | Trashigang | Lungtenzampa | NI | 3 legged | 30m | 10 minutes | 15Km from Trashigang | 5750 | Yes | Yes
25 | SWR | Gedu | Damjekha | NI | 3 legged | 25m | 30mins | 50KM | 4450 | Yes | Yes
26 | SWR | Gedu | Bjachhog | NI | 3 legged | 25m | 10mins | 20KM | 4450 | Yes | Yes
27 | SWR | Pling | Lokchina | NI | 3 legged | 30m | 30mins | 37KM | 5750 | Yes | Yes
28 | SWR | Samtse | Dhamdhum Industrial Park | NI | 4 legged | 40m | 5mins | 3KM | 10000 | Yes | Yes
29 | SWR | Samtse | Alaypakha | NI | 3 legged | 30m | 30mins | 5KM | 5750 | Yes | Yes
30 | SWR | Pling | Pakchina (Highway) | NI | 3 legged | 30m | 30mins | 37KM | 5750 | Yes | Yes
31 | WR | Paro | Bondey (Dantak) | NI | 3 legged | 30m | Near road | 7km | 5750 | Yes | Yes
32 | WR | Paro | Bjanagu | NI | 3 legged | 20m | 1 Hour | 20km | 3550 | Yes | Yes
33 | WR | Wangdi | Khelikha | NI | 3 legged | 30m | 10mins | 17km | 5750 | Yes | Yes
34 | WR | Wangdi | Rutokha | NI | 3 legged | 30m | 20mins | 3km | 5750 | Yes | Yes
35 | WR | Wangdi | Khujula | NI | 3 legged | 25m | 20mins | 15km | 4450 | Yes | Yes
36 | WR | Punakha | Zhelngosa | NI | 3 legged | 25m | 30mins | 52km | 4450 | Yes | Yes
37 | WR | Punakha | Khilikhar | NI | 3 legged | 25m | 30mins | 16km | 4450 | Yes | Yes
38 | WR | Haa | Near Jampel School | NI | 3 legged | 30m | 20mins | 11km | 5750 | Yes | Yes
39 | CR | Dagapela | Namchela RS | NI | 7M Monopole | 20m | 3MINS | 55km | 3550 | Yes | Yes
40 | CR | Damphu | Dhajay top | NI | 20M 3 legged | 35m | 60 MINS | 28km | 7750 | Yes | Yes
41 | CR | Gelephu | Samkhara BTS | NI | 15M 3 legged | 30m | NO | 42km from gelephu | 5750 | Yes | Yes
42 | ER | Lhuntse | Ganglapong | NI | 12m VNL | 25m | 15mins | 55km | 4450 | Yes | Yes
43 | ER | Nganglam | Rinchenzor | NI | 12m VNL | 25m | 15mins | 28km | 4450 | Yes | Yes
44 | ER | Sjongkhar | Merinchengmo | NI | 12m VNL | 25m | More than 2 Hour | 72km | 4450 | Yes | Yes
45 | ER | Trashigang | Changmey | NI | WLL Monipole | 25m | 5 minutes | 25Km from Trashigang | 4450 | Yes | Yes
46 | ER | Tashiyangtse | Gimorong(Bumdeling) | NI | 12m Monopole | 25m | 10mins | 15km | 4450 | Yes | Yes
47 | ER | Tashiyangtse | Gangadung | NI | 15m, 3-legged | 25m | 1hr | 1km | 4450 | Yes | Yes
48 | SWR | Gedu | Gedu town | NI | 24M | 35m | 20 MINS | 2KM | 7750 | Yes | Yes
49 | WR | Thimphu | Simtokha Exch | NI |  | 30m | 10mins | 2km | 5750 | Yes | Yes

## Shelter Replacement
Sl.No | Region | PC | Site Name | Infra Type | Proposed Technology | Shelter Type | Total Wight (Kg) | Headload (from nearest roadpoint) | Distance from main road KM(Approx) | Transporation of shelter and foundation materials to designated site price | Shelter Erection including earthing price | Transporation of AC Power materials materials to designated site price | Installation of Power Materials
| SWR | Samtse | Dhamdhum Industrial Park | NI | LTE1800+2G | Pre-Fab | 1300 | 2600 | 5mins, 3KM | Yes | Yes | Yes | Yes
| WR | Thimphu | Thimphu Exchange | NA | NA | Pre-Fab | 2200 | 2600 | Near road, Inside CHQ, Thimphu | Yes | Yes | Yes | Yes
| WR | Paro | Bondey (Dantak) | NI | LTE1800+2G | Pre-Fab | 1300 | 2600 | Near road, 7Km | Yes | Yes | Yes | Yes
1 | ER | Sjongkhar | Jomotshangkha BTS | EI | Shelter replacement | Pre-Fab | 1300 | near road | 1.5km | Yes | Yes | 0 | 0
2 | ER | Sjongkhar | Monmola | EI | Shelter replacement | Pre-Fab | 1300 | 2 hurs | 28KM | Yes | Yes | 0 | 0
3 | ER | Sjongkhar | Agurthang | EI | Shelter replacement | Pre-Fab | 1300 | 10mins | 11Km | Yes | Yes | 0 | 0

## Monopole
Sl.No | Region | PC | Site Name | Infra Type | Proposed Technology | Sector | Pole Type | Pole Height | Qty of LED Lamp (nos) | Monopole Weight (Kg) | Transporation of Monopole and foundation materials to designated site | Monopole Erection including earthing and lighting
1 | CR | Bumthang | FMCL | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
2 | CR | Bumthang | Tharpaling | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
3 | CR | Gelephu | Royal Guest house new (Raidara) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
4 | CR | Gelephu | Dechenpelri School | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
5 | CR | Gelephu | Patsheling Dratshang | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
6 | CR | Gelephu | Lodruk Choeling Buddhist Institute | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
7 | CR | Trongsa | Yurmung BPC colony | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
8 | CR | Trongsa | Drakteng Gewog office | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
9 | CR | Zhemgang | Sonamthang | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
10 | CR | Gelephu | NPPF Colony | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
11 | CR | Gelephu | Workshop area | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
12 | ER | Lhuntse | Namdruling Dratsang | NI-D | LTE1800 +2G MM | 3 | Flange joint | 15m | 3 | 1350 | Yes | Yes
13 | ER | Mongar | Trailing | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
14 | ER | Sjongkhar | Nyalang | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
15 | ER | Sjongkhar | Sjk Hospital | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
16 | ER | Trashigang | Pam Village | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
17 | ER | Trashigang | Kanglung Namla | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
18 | ER | Trashigang | Gongthung HSS | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
19 | ER | Trashigang | Yangner Gewog | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
20 | ER | Trashiyangtse | Gomkora | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
21 | SWR | Gedu | Gedu town/Bitdeer Mining center | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
22 | SWR | Gedu | Laptshakha | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
23 | SWR | Pling | NHDCL Colony, Toorsa | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
24 | SWR | Pling | Pipal dara 2 | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
25 | SWR | Pling | Malbasay BPC Colony | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
26 | SWR | Pling | Milarepa Lhakhang | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
27 | SWR | Pling | Wangdue Gatshel Family Line | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
28 | SWR | Samtse | Sibsoo New Hospital | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
29 | SWR | Samtse | Tata Colony (Pugli) | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
30 | SWR | Samtse | Chengmari town | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
31 | SWR | Samtse | Tendu Bazaar | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
32 | SWR | Samtse | Singyegang (Sibsoo) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
33 | SWR | Samtse | Namgaycholing | NI-D | LTE1800 +2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
34 | SWR | Pling | Majigaon | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
35 | WR | Haa | Takchu Goenpa | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 2 | 1250 | Yes | Yes
36 | WR | Haa | Juneydra Palace | NI-D | LTE1800+2G MM | 3 | Flange joint | 15m | 3 | 1350 | Yes | Yes
37 | WR | Wangdi | Tsira/Basachu Colony | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
38 | WR | Thimphu | Talakha (VVIP-Cabinet) | NI-D | LTE1800+2G MM | 3 | Flange joint | 15m | 3 | 1350 | Yes | Yes
39 | WR | Punakha | Yangchikha | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | NO | 1250 | Yes | Yes
40 | WR | Gasa | Laya | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | NO | 1250 | Yes | Yes
41 | WR | Paro | Geptey/Tsendona (Drangja) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
42 | WR | Punakha | Exchange-Cabinet | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
43 | SWR | Pling | Pemaling NHDCL (As a replacement of Exchange TDD) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
44 | SWR | Pling | Dolma (As a replacement of Dantak TDD) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
45 | SWR | Samtse | PCA Colony/Main gate (As a replacement of Gomtu town TDD) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
46 | ER | SJK | NPPF Housing Colony (As a replacement of Exchange TDD) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes
47 | ER | SJK | Town BPC Area (As a replacement of Dantak TDD) | NI-D | LTE1800+2G MM | 3 | Slip joint | 15m | 3 | 1250 | Yes | Yes